## Description of PWS
SYSTEM DESCRIPTION
Water District; PWSID # 0909000
CWS source and treatment consists of one groundwater well. The well water is pumped to the treatment facility where it
encounters the following steps; Potassium permanganate oxidized anthracite and green sand filtration, then anthracite, sand and garnet
multi-media filtration, then granular activated carbon filtration to remove taste and odor, then addition of orthophosphate for corrosion control,
and finally liquid hypochlorination to attain free residual disinfection.
Storage consists of one (1) 185,000 gallon welded steel ground level tank.
Pressure is maintained as one (1) pressure zone by three ten horsepower 150 gpm variable frequency drive pumps.
There is only one entry point (EP001) to the distribution system located at the treatment facility. See picture in "TCR Triggered
and EP001 Sites".
There are forty-eight (48) residential service connections serving ~210 year round residents and three (3) commercial connections.
RCAC Circuit Rider (technical assistance) Contact: Randy Vessels, cell# (916) 838-7061, rvessels@rcac.org OR
Lee Schegg, Cell # (916) 704-8134, lschegg@rcac.org
The SWRCB Program Manager is: A. Toughdude and may be reached at (415) 972-9999, AToughdude@ca.gov
The lab contact info is: Alpha Analytical Lab, 208 Mason Street, Ukiah, CA 95482, Phone: 707.468.0401, FAX: 707.468.5267,
clientservices@alpha-labs.com
Date: 01-19-2015

## Monitoring Schedule
Water District; PWS# 0909000
Contaminant Group | Required Sampling Frequency | Map Location (see legend for specific addresses)
Routine Total Coliform | SWRCB Required 3 samples / month [District chooses to take four (4)] | Three (3) samples due each month (S1 thru S8) [District chooses to take four (4)]
Repeat Total Coliform | 4 Samples taken within 24 hours of notice of a total coliform result. Sample at original site, upstream and downstream within five (5) connections, AND the raw water source (before treatment). | Use corresponding Upstream, Downstream and Source on TCR Legend
Original S# Site
Upstream R Odd #
Downstream R Even #
GWR -Raw Well Source
Increased Total Coliform | 5 samples taken in the month following a routine positive sample. Replaces routine total coliform sampling | Use five (5) Sites S1 thru S8 (include the original coliform positive site)
Chlorine Residual | Sample taken with every TCR routine or repeat sample | At each TCR sample location; field test.
Lead (Pb) & Copper (Cu) | 10 samples every year. NOTE: Sample between June 1 and September 30 | Pb/Cu Site #1 thru #10 - Take one (1) sample from each sample site
DBP Stage 2 (TTHM & HAA5) | 1 sample every year. NOTE: Sample in August | Sample for Stage 2 DBPR at Housing Repeat Site R3
Water Quality Parameters (WQP) | Collect a field sample twice yearly (every six months) | Sample at Housing Office (Address?) (R3)
Nitrate | 1 sample every year. | EP001
Inorganic Chemicals (IOCs) | Sample IOCs every three (3) years. NOTE: Cyanide is waived and requires recertification every nine (9) years | EP001
Volatile Organic Chemicals (VOCs) | Sample every three (3) years. | EP001
Synthetic Organic Chemicals (SOCs) | Sample every three (3) years. | EP001
Dioxin (2,3,7,8-TCDD) | Waiver in effect | Renew waiver every three (3) years.
Radionuclides | Sample Adjusted Alpha, Combined Radium 226/228 and Uranium every nine (9) years | EP001
Asbestos | Sample every nine (9) years | 570 Brown Water (R3)
Shading indicates contaminant group for which a site sampling plan is required.
Laboratory:
Alpha Analytical Labs, 208 Mason Street, Ukiah CA, 95482, Phone: 707.468.0401
Notes:
1) This Monitoring Schedule is for planning purposes and should represent actual requirements,
however the most recent Monitoring Schedule and Compliance Report from your SWRCB Program
Manager is the official schedule of monitoring requirements.

## TCR Housing DBP and WQP Map
Insert Your Map Information on this Page

## TCR Housing Map Detail
Insert Your Sampling Location Detail Map on this Page

## TCR Hotel Map
Insert Your Sampling Location Detail Map on this Page

## TCR RV Park Map
Insert Your Sampling Location Detail Map on this Page

## PbCu Siting Map
Insert Your Sampling Location Detail Map on this Page

## TCR Triggered and EP001 Sites
Insert Your Sampling Location Detail Map on this Page

## TCR Legend
COLIFORM BACTERIA SAMPLE SITING PLAN |  |  |  | APPROVED by SWRCB on :
PWS NAME: |  | Water District |  | WATER SOURCES:
PWS ID#: |  | #0909000 |  | Source Well
DATE: |  | 2015-01-19
| LIST OF SAMPLING SITES |  | SAMPLING SITE ROTATION
No. | SITE ID# | SITE NAME/ADDRESS | MONTH | SITE ID#
1 | S1 | 590 Lois Lane (Dedicated Tap) | January | S1, S3, S6, S8
2 | R1 | 570 Lois Lane | February | S2, S4, S7, S8
3 | R2 | 595 Lois Lane | March | S1, S5, S6, S8
4 | S2 | 2975 Farley Lane | April | S2, S3, S7, S8
5 | R3 | 3115 Farley Lane (Dedicated tap) | May | S1, S4, S6, S8
6 | R4 | 2935 Farley Lane | June | S2, S5, S7, S8
7 | S3 | RV Park Available Site 2-26 | July | S1, S3, S6, S8
8 | R5 | RV Park Available Site 43-44 | August | S2, S4, S7, S8
9 | R6 | RV Employee Lounge Sink | September | S1, S5, S6, S8
10 | S4 | RV Park Available Site 27-42, 45-62 | October | S2, S3, S7, S8
11 | R5 | RV Park Available Site 43-44 | November | S1, S4, S6, S8
12 | R6 | RV Employee Lounge Sink | December | S2, S5, S7, S8
13 | S5 | RV Park Available Site 63-74
14 | R5 | RV Park Available Site 43-44 | Required Routine Samples per Month: 3
15 | R6 | RV Employee Lounge Sink | Following a sample with total/fecal contamination:
16 | S6 | Hotel Employee Lounge Sink | Collect 4 repeats samples within 24 hours.
17 | R5 | RV Park Available Site 43-44 | • One (1) Original and two (2) Repeat Sites
18 | R8 | Hotel Employee Restroom Sink |  | (Upstream and Downstream)
19 | S7 | Hotel Kitchen Hand Sink | • One (1) Repeat Sample from Wellhead
20 | R5 | RV Park Available Site 43-44 | Collect 5 routine samples the next month.
21 | R6 | RV Employee Lounge Sink | Repeat Sampling Sites: Original, upstream and
22 | S8 | Hotel Employee Restroom Sink | downstream. | Label as Repeat Samples
23 | R6 | RV Employee Lounge Sink | Repeat from well - Collect at well (pre-chlorination)
24 | R7 | Available Hotel Room 101-190 | Label as GWR Compliance Sample
25 | GWR | Triggered Site at Well Pump House | The following month: 5 Routine Sampling Sites:
|  | (see picture in "TCR Triggered Tab") | Use five sites as shown in schedule

## PbCu Legend
LEAD AND COPPER SAMPLE SITING PLAN |  | APPROVED by SWRCB on :
PWS NAME: | Water District
PWS ID#: | #0909000
DATE: | 2014-12-19
LIST OF Pb and Cu SAMPLING SITES |  | 1) Samples are taken "first draw"
SITE ID# | SITE NAME | from taps that have been closed
PbCu #1 | 590 Lois Lane | overnight or at least 6 hours.
PbCu #2 | 570 Lois Lane | 2) Samples taken every year.
PbCu #3 | 540 Lois Lane | 3) Samples are to be taken between 6/1 and 9/30.
PbCu #4 | 520 Lois Lane | 4) Samples outside this period will be invalid.
PbCu #5 | 500 Lois Lane | 5) Pull one (1) sample from each Site #1 - #10
PbCu #6 | 2920 Farley Lane
PbCu #7 | 2930 Farley Lane
PbCu #8 | 3145 Farley Lane
PbCu #9 | 3105 Farley Lane
PbCu #10 | 3125 Farley Lane

## DBPR and Chem Legend
Disinfection By-Products Rule and Misc. Chemical Rules |  | APPROVED by SWRCB on :
PWS NAME: | Water District
PWS ID#: | #0909000
DATE: | 2014-12-19
List of Stage 2 DBPR SAMPLING SITES
SITE ID# | SITE NAME | Storet ID#
Stage 2 DBPR | 570 Lois Lane (TCR Repeat Site R3)
Location of Daily Water Quality Parameter Sampling Site
SITE ID# | SITE NAME | Storet ID#
WQP | 570 Lois Lane (TCR Repeat Site R3)
List of Nitrate, IOCs, VOCs, SOCs, & Radionuclide Sites
SITE ID# | SITE NAME | Storet ID#
EP001 | EP001 Site (labeled inside treatment facility)
Location of Asbestos Sampling Site
SITE ID# | SITE NAME | Storet ID#
TCR R3 Site | 570 Lois Lane (TCR Repeat Site R3)